## DAPR Projects 5yr view (2024)
Field Name | Rule | Data Type | Units | Other information
Project ID |  | Text |  | Project number | NPR-000044 | NPR-000070 | NPR-000951 | NPR-000048 | NTM-000535 | NPR-000069 | NPR-000049
Asset Name |  | Text |  | Substation or feeder name(s) | Lowes Creek ZS | Box Hill ZS | Menangle Park ZS | Grantham Farm ZS | 132kV Oil Cable Replacement | West Appin ZS | Mt Gilead ZS
Constraint primary driver | DT001 | Text |  | Choose one of: capacity; reliability; asset condition; performance; safety; environment; power quality; voltage | Capacity | Capacity | Capacity | Capacity | Reliability & Safety & Environment | Capacity | Capacity
Location of constraint (start) | DT002 | Decimal | Lattitude° ,Longitude° |  | - 33°58'47.80", 150°44'6.35" | -33.637224, 150.898978 | -34.093151, 150.751829 | -33.663998, 150.893481 | -33.824824, 151.030938 | 34°12'12.83"S, 150°46'17.15"E | -34.139089, 150.769423
Location of constraint (end) | DT003 | Decimal | Lattitude° ,Longitude° |  | - 33°58'47.80", 150°44'6.35" | -33.637224, 150.898978 | -34.093151, 150.751829 | -33.663998, 150.893481 | -33.824824, 151.030938 | 34°12'12.83"S, 150°46'17.15"E | -34.139089, 150.769423
Asset ID | DT004 | Text |  | Consistent with RIN Sustained Interruptions sheet from Category Analysis template | NPR-000044 Lowes Creek ZS Establishment | NPR-000070 Augmentation of Box Hill ZS | NPR-000951 Augmentation of Menangle Park ZS | NPR-000048 Establishment of Grantham Farm ZS | Replacement of end of life 132kV oil filled cables in the Parramatta area | NPR-000069 Establishment of West Appin ZS | NPR-000049 Establishment of Mt Gilead ZS
Network Element | DT005 | Text |  | Choose one of: Transmission connection point; zone substation; sub-transmission line; feeder | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Sub-transmission Line | Zone Substation | Zone Substation
Residential customers affected | DT006 | Integer | Total number of customers affected |  | <1000 | >1000 | >1000 | >1000 | >1000 | >1000 | >1000
Residential customers affected | DT006_a | Decimal | % of total customers affected |  | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Voltage level | DT009 | Decimal | KV | Highest operational voltage level of the assets involved in the constraints | 132 | 132 | 66 | 132 | 132 | 66 | 66
Preferred network investment | DT012 | Text |  | Brief description: Free text | Establish new ZS | Augment existing ZS | Augment existing ZS | Establish new ZS | Replace cables at end of life with modern equivalent of increased capacity | New ZS within the West Appin area | New ZS within the Gilead Precinct
Preferred network investment capital cost | DT013 | Decimal | $ (real) |  | 40000000 | 25000000 | 40000000 | 40000000 | 41800000 | 40000000 | 40000000
Preferred annual network investment operating cost | DT013_a | Decimal | $ (real) | Annual operating costs (including overheads, risk allowance and contingency allowance if included) | 160000 | 100000 | 160000 | 160000 | 167200 | 160000 | 160000
Preferred network investment cost accuracy | DT014_a | Decimal | +% |  | 20 | 20 | 20 | 20 | 20 | 20 | 20
Preferred network investment cost accuracy | DT014_b | Decimal | -% |  | 20 | 20 | 20 | 20 | 20 | 20 | 20
Proposed timing FNY | DT015 | Date | MM/YYYY |  | FY27 | FY28 | FY27 | FY27 | FY29 | FY28 | FY29
Demand reduction required to defer investment by 1 year | DT016 | Decimal | MVA | MVA | 20 | 5 | 10 | 20 | N/A | 10 | 10
Demand reduction required to defer investment by 1 year | DT016_a | Decimal | MW | If MW data is collected | 20 | 5 | 10 | 20 | N/A | 10 | 10
Annual Deferral Value | DT017 | Decimal | $ (real) | Using an appropriate VCR as an input | 1308000 | 817500 | 1308000 | 1308000 | 1366860 | 1308000 | 1308000
Load transfer capability | DT017 | Decimal | MVA | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load transfer capability | DT017_a | Decimal | MW | If MW data is collected | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency generation | DT018 | Decimal | MVA | MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency generation | DT018_a | Decimal | MW | If MW data is collected | 0 | 0 | 0 | 0 | 0 | 0 | 0
Historic use of existing emergency response | DT019 | Series | DD/MM/YYYY HH:MM; MVA |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic use of existing emergency response | DT019_a | Series | DD/MM/YYYY HH:MM; MW | If MW data is collected | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic asset rating | DT021 | Series | HH:MM DD/MM/YYYY MVA; | 3 years historic, 30 minute intervals uncleansed | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic asset rating | DT021_a | Series | HH:MM DD/MM/YYYY MW; | 3 years historic; 30 minute intervals, uncleansed | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Forecast Load Energy at Risk_24
| Project ID | NPR-000044 | NPR-000070 | NPR-000951 | NPR-000048 | NTM-000535 | NPR-000069 | NPR-000049
| Asset Name | Lowes Creek ZS | Box Hill ZS | Menangle Park ZS | Grantham Farm ZS | 132kV Oil Cable Replacement | West Appin ZS | Mt Gilead ZS
| Asset ID | NPR-000044 Lowes Creek ZS Establishment | NPR-000070 Augmentation of Box Hill ZS | NPR-000951 Augmentation of Menangle Park ZS | NPR-000048 Establishment of Grantham Farm ZS | Replacement of end of life 132kV oil filled cables in the Parramatta area | NPR-000069 Establishment of West Appin ZS | NPR-000049 Establishment of Mt Gilead ZS
Asset Rating (MVA firm) | Year
| 2026 | 45 | 36 | 5.67 | 95 | 0 | 0 | 7.94
| 2027 | 45 | 36 | 5.67 | 95 | 0 | 0 | 7.94
| 2028 | 45 | 36 | 5.67 | 95 | 0 | 0 | 7.94
| 2029 | 45 | 36 | 5.67 | 95 | 0 | 0 | 7.94
| 2030 | 45 | 36 | 5.67 | 95 | 0 | 0 | 7.94
Asset Rating (MW firm) Formula, assuming a PF | Year
| 2026 | 42.75 | 34.2 | 5.3865 | 90.25 | 0 | 0 | 7.543
| 2027 | 42.75 | 34.2 | 5.3865 | 90.25 | 0 | 0 | 7.543
| 2028 | 42.75 | 34.2 | 5.3865 | 90.25 | 0 | 0 | 7.543
| 2029 | 42.75 | 34.2 | 5.3865 | 90.25 | 0 | 0 | 7.543
| 2030 | 42.75 | 34.2 | 5.3865 | 90.25 | 0 | 0 | 7.543
Forecast Demand 50% POE (MVA) | Year
| 2026 | 65.509 | 30.495 | 10.78 | 88 | 0 | 11.5506 | 3.6502
| 2027 | 62.9671 | 36.4736 | 14.27 | 98.2 | 0 | 16.0236 | 4.9462
| 2028 | 73.7962 | 43.7278 | 17.75 | 107.6 | 0 | 19.9345 | 6.6742
| 2029 | 84.8874 | 48.3813 | 21.45 | 117.2 | 0 | 24.066 | 9.2662
| 2030 | 96.5787 | 53.0347 | 24.73 | 121.6 | 0 | 30.2723 | 12.4982
Forecast Demand 50% POE (MW) Formula, assuming a PF | Year
| 2026 | 62.2336 | 28.9703 | 10.241 | 83.6 | 0 | 10.9731 | 3.4677
| 2027 | 59.8188 | 34.65 | 13.5565 | 93.29 | 0 | 15.2224 | 4.6989
| 2028 | 70.1064 | 41.5414 | 16.8625 | 102.22 | 0 | 18.9378 | 6.3405
| 2029 | 80.6431 | 45.9622 | 20.3775 | 111.34 | 0 | 22.8627 | 8.8029
| 2030 | 91.7497 | 50.383 | 23.4935 | 115.52 | 0 | 28.7586 | 11.8733
Forecast Demand 10% POE (MVA) | Year
| 2026 | 65.509 | 30.495 | 10.78 | 19.1 | 0 | 11.5506 | 3.6502
| 2027 | 62.9671 | 36.4736 | 14.27 | 23.5 | 0 | 16.0236 | 4.9462
| 2028 | 73.7962 | 43.7278 | 17.75 | 27.9 | 0 | 19.9345 | 6.6742
| 2029 | 84.8874 | 48.3813 | 21.45 | 30.3 | 0 | 24.066 | 9.2662
| 2030 | 96.5787 | 53.0347 | 24.73 | 32.8 | 0 | 30.2723 | 12.4982
Forecast Demand 10% POE (MW) Formula | Year
| 2026 | 62.2336 | 28.9703 | 10.241 | 18.145 | 0 | 10.9731 | 3.4677
| 2027 | 59.8188 | 34.65 | 13.5565 | 22.325 | 0 | 15.2224 | 4.6989
| 2028 | 70.1064 | 41.5414 | 16.8625 | 26.505 | 0 | 18.9378 | 6.3405
| 2029 | 80.6431 | 45.9622 | 20.3775 | 28.785 | 0 | 22.8627 | 8.8029
| 2030 | 91.7497 | 50.383 | 23.4935 | 31.16 | 0 | 28.7586 | 11.8733
Maximum Load at risk (MW) Formula | Year
| 2026 | 19.4836 | -5.2297 | 4.8545 | -6.65 | 0 | 10.9731 | -4.0753
| 2027 | 17.0688 | 0.44996 | 8.17 | 3.04 | 0 | 15.2224 | -2.8441
| 2028 | 27.3564 | 7.3414 | 11.476 | 11.97 | 0 | 18.9378 | -1.2025
| 2029 | 37.8931 | 11.7622 | 14.991 | 21.09 | 0 | 22.8627 | 1.2599
| 2030 | 48.9997 | 16.183 | 18.107 | 25.27 | 0 | 28.7586 | 4.3303
Expected Unserved Energy (MWh) | Year
| 2026 | 3.4313 | 0 | 4.1525 | 1.7599 | 0 | 2.7268 | 0
| 2027 | 2.5612 | 0.00073412 | 32.8452 | 5.2458 | 0 | 14.3337 | 0
| 2028 | 7.6249 | 0.26938 | 411.108 | 10.4921 | 0 | 150.6762 | 0
| 2029 | 18.6804 | 12.678 | 3859.6247 | 18.6461 | 0 | 540.4438 | 0.042131
| 2030 | 69.7591 | 101.6584 | 7137.0764 | 23.2959 | 0 | 2183.1524 | 66.4213